## Lighting Fixture Schedule
VASSAR TOWER EXPANSION LIGHTING FIXTURE SCHEDULE
TYPE | LOCATION | DESCRIPTION | MANUFACTURER | CATALOG NUMBER | FINISH | LAMP DATA |  |  | Fixture Wattage | INPUT WATTS | VOLTS | NOTES
[6 empty] | NO. | WATTS | TYPE
EX1 | General | Single face, universal mount, edgelit LED emergency exit sign with high impact acrylic panel with nickel cadmium battery | Sure-Lite | #ELX7-1-70-00-FINISH-R-XX | Per Arch | 1 | 4.8 | LED |  | 4.8 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on electrical plans
EX2 | General | Double face, universal mount, edgelit LED emergency exit sign with high impact acrylic panel with nickel cadmium battery | Sure-Lite | #ELX7-2-70-00-FINISH-R-XX | Per Arch | 1 | 4.8 | LED |  | 4.8 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on electrical plans
EX3 | General | Single face, universal mount, AC, die-cast aluminum LED exit sign | Surelite Prescolite Dualite | #CAX6-1-00-R-FINISH | Per Arch | 1 | 4 | LED |  | 4 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on electrical plans
EX4 | General | Double face, universal mount, AC, die-cast LED exit sign | Surelite Prescolite Dualite | #CAX6-2-00-R-FINISH | Per Arch | 1 | 4 | LED |  | 4 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on electrical plans
EX5 | Roof | Weather proof Led exit sign | Surelite Prescolite Dualite | UX6-0/1-95-R-FINISH | Per Arch | 1 | 4 | LED |  | 4 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on electrical plans
FA | Patient Rooms | Recessed nominal 8" x 4' x 5"D, 3-circuit, ambient, exam and reading functions with 3000K LED, white aluminum reflector, frosted acrylic lens; on board drivers and anti-microbial white powder coat painted steel housing with integral 0-10V dimming drivers | Failsafe Kenall | #MNAE-G-48-LD4-STD-HI-30-89DA-CRSW-277V-EDD2-IP65-SRL/L & SRL/R | White | 1 | 87.5 | LED (3000K) |  | 87.5 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FAA | Emergency Department Exam Rooms, Bariatric, Dialysis | Similar to type "FA", except 2-circuit with Exam and Ambient function | Failsafe Kenall | #MNAE-G-48-LD4-STD-HI-30-89DA-CRSW-277V-EDD2-IP65 | White | 1 | 80 | LED (3000K) |  | 80 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FA1 | Offices, Case Management, Physician Workroom, Results Waiting, Consult | Recessed nominal 2' x 2' x 6" ambient troffer with approximately 3300 output lumens, 3000K LED, curved white reflector, central perforated basket with acrylic overlay,white steel housing with, integral 0-10V dimming driver | Lithonia Neoray Eaton Philips | #2AVL2-CLG-30L-MDR-EZ1-LP830 | White | 1 | 36 | LED (3000K) |  | 36 | 120-277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Provide local dimmer switch as per plans
FA1A | ISO Rooms, ED Ante Rooms; Anesthesia Workroom, Frozen Sections, Decon.; ED Iso soil | Recessed, nominal 1' x 4' x 6" ambient troffer with 3000K LED, patterned acrylic lens, anti-microbial white painted steel housing, gasket kit and integral 0-10V dimming driver. Provide overlap flange in GWB ceilings | Eaton Fail Safe Healthcare Lighting Certolux | #CLPF/G-12-4-ALH-INS/OLS-A12125-LD4-2-HI-30-277-ED1D-1-AMA | White | 1 | 95 | LED (3000K) |  | 95 | 277 | • Contractor to coordinate all mounting requirements including flange with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FA2 | Soiled Holding, Clean Supply, Clean Corridors, CCU Iso; Procedure Rooms; Pump Room, Low Temp Sterilization | Recessed nominal 2' x 2' x 3-1/2" ambient troffer with 3000K LED, approximately 3000 fixture lumens, opal acrylic lens, fully sealed & gasketed, with white anti-microbial paint white steel housing, integral power supply with 0-10V driver. Provide overlap flange where fixture resides in gwb ceiling | Corelite Lithonia Focal Point | #R2X-W-O-3-L30-1-C-277-22-CLG-AM-LG | White | 1 | 38 | LED (3000K) |  | 38 | 120/277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture shall be switched
FA3 | Med Waste, Soiled Holding, Frozen Section, Clean Supply | Recessed nominal 2' x 4' x 3-1/2" ambient troffer with 3000K LED, approximately 6500 fixture lumens opal acrylic lens, fully sealed & gasketed, with white anti-microbial paint white steel housing, integral 0-10V driver | Corelite Lithonia Focal Point | #R2X-W-O-4-L30-1-C-277-24-CLG-AM-LG | White | 1 | 75 | LED (3000K) |  | 75 | 120/277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture shall be switched
FA4 | Psych Evaluation, B2 Prisoner Holding | Recessed, nominal 1' x 4' x 5-1/2" ambient, vandal-resistant 3500K LED troffer with prismatic polycarbonate lens; approximately 4900 fixture lumens, gasket kit, white steel housing with overlap flange; integral 0-10V driver | Fail-Safe Healthcare Lighting Kenall | #FMR-S-12-4-LD4-2-STD-35-UNV-80-84-EDC-1-WL-SSP-VRSD | White | 1 | 73 | LED (3500K) |  | 73 | UNV | • Contractor to coordinate all mounting requirements with specified ceiling system. • Provide with overlap flange in 1st floor rooms • Fixture shall be switched
FA5 | Corridors, B2 Staff Lounge, Staff Lockers; Nourishment, Hallways (non-patient corridors); Soiled workroom; Ultrasound; Ortho Gym | Recessed, nominal 2' x 2' x 3-1/2" ambient troffer, with 3000K LED, approximately 3300 fixture lumens, opal acrylic lens, white steel housing and integral 0-10V driver | Corelite Lithonia Focal Point | #R2X-W-O-3-L30-1-C-277-22-CLG | White | 1 | 38 | LED (3000K) |  | 38 | 120/277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture shall be switched
FA6 | TAVR Rm | Recessed, nominal 1' x 4' x 6" ambient troffer with 5000K LED; approximately 7500 fixture lumens, acrylic lens; gasket kit, steel housing with overlap flange, white anti-microbial paint and integral 0-10V dimming driver | Eaton Fail Safe Healthcare Lighting Certolux | #CLPG-12-4-OLS-A12125-LD4-2HI-50-277-ED1D-AMA | White | 1 | 94 | LED (5000K) |  | 94 | 120/277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FA7 | CCU Patient Room | Recessed nominal 2' x 2' x 3-1/2", ambient troffer with 3000K LED, approximately 4000 fixture lumens, opal acrylic lens; white steel housing with anti-microbial paint and integral 0-10V dimming driver | Corelite Lithonia Focal Point | #R2X-W-O-4-L30-1-D-277-22-CLG-AM | White | 1 | 49 | LED (3000K) |  | 49 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FA8 | Phase II Recovery, Isolation Phase II Recovery, Isolation PACU | Similar to type "FA", except 1-circuit with Exam function. Provide overlap flange in rooms with gwb ceiling | Failsafe Kenall | #MNAE-G-48-LD4-HI-30-89DA-CRSW-277V-EDD1-IP65-DFCL AS REQ'D. | White | 1 | 45 | LED (3000K) |  | 45 | 120V in existing bldg; 277 in new | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FA9 | Med Prep | Recessed nominal 2' x 4' x 5" ambient troffer with 3000K LED, approximately 10,000 fixture lumens frosted acrylic lens, with white anti-microbial paint white steel housing, integral 0-10V driver | Failsafe | #MAO-G-4-LD4-3-STD-30-UNV-EDD-1-FA-AM | White | 1 | 110 | LED (3000K) |  | 110 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FB | BOH | Ceiling; wall or chain mounted nominal 3"W X 4"H X 2' or 4'L 3000K LED striplight with approximately 1100 fixture lumens per L.F., frosted lens, white steel housing and integral 0-10V dimming driver | Metalux Lithonia | #2/4SNLED-LD4-46SL-LW-UNV-L830-CD-1-AYC-CHAIN/SET AS REQ'D. | White | 1 | 12.5/lf | LED (3000K) |  | 12.5/lf | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling and/or wall system. • Provide chainset as required • Fixture shall be switched
FB1 | BOH Equipment storage, EVS | Recessed, nominal 2' x 2' x 4" ambient troffer with 3000K LED, approximately 2000 fixture lumens, prismatic acrylic lens, white steel housing and 0-10V driver | Metalux Corelite | #22-G-R-FA-LD4-20-F1-UNV-L830-CD-1-PAF | White | 1 | 20 | LED (3000K) |  | 20 | UNV | • GC to coordinate with approved ceiling system. • Fixture shall be switched
FB2 | Loading Dock Corridor | Surface mounted, nominal 5"H x 8"H x 4'L wet location, 3000K LED strip with approximately 4000 fixture lumens, clear acrylic lens, gasket, fiberglass housing with stainless steel latches | Mercury Lighting Lithonia | #L501-4-4200-30K-AIM-U-UNI-SSL | White | 1 | 41 | LED (3000K) |  | 41 | 120-277 | • Contractor shall coordinate all mounting reqirements with specified ceiling or wall system. • Provide all mounting brackets as required
FB3 | BOH, Clean Storage | Recessed, nominal 2' x 4' x 4" ambient troffer with 3000K LED, approximately 3800 fixture lumens, prismatic acrylic lens, white steel housing, 0-10V driver | Metalux Corelite Lithonia | #24-G-R-FA-LD4-38-F1-UNV-L830-CD-1-PAF | White | 1 | 35 | LED (3000K) |  | 35 | 120-277 | • Contractor shall coordinate all mounting reqirements with specified ceiling • Fixture shall be switched
FB4 | Kitchen, Servery | Recessed, nominal 2' x 2' x 4" ambient troffer with 3000K LED, approximately 4800 fixture lumens, prismatic acrylic lens, white steel housing, triple gasket kit and 0-10V driver | Mercury Lithonia Metalux | #LR34-22G-4800-30K-9A-UXX-UNI-TG | White | 1 | 51 | LED (3000K) |  | 51 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FB5 | Boiler Plant | Kindorf mounted nominal 15"w x 4'L X 7"h vaportight industrial area light with 4000K LED, approximately 19,000 fixture lumens, metal gear tray, high-impact clear acrylic lens stainless steel mounting brackets, integral driver | Metalux Lithonia | #VT4LED-LD4-19-DR-120-L840-ED-2-WL-SSL-VT4LED-SS-MKB-PK | White | 1 | 140 | LED (4000K) |  | 140 | 120 | • Contractor to coordinate all mounting requirements & provide necessary hardware • Fixture is mounted to kindorf • Connect to inverter for EM function
FB6 | Shed | Surface mounted, nominal 5"H x 8"H x 4'L wet location, 3000K LED strip with approximately 4000 fixture lumens, clear acrylic lens, gasket, fiberglass housing with stainless steel latches with integral photocell | Mercury Lighting Lithonia | #L501-4-4200-30K-AIM-U-UNI-SSL-PC | White | 1 | 41 | LED (3000K) |  | 41 | 120-277 | • Contractor shall coordinate all mounting reqirements with specified wall system. • Provide all mounting brackets as required
FC | Patient Rooms, Typical Patient Floor Care Center | Surface mounted, nominal 2"w x 2-1/2"h continuous, adjustable 3000K warm white LED strip with flood distribution, approximately 400 lumens per l.f., with remote power supply and 0-10V dimming driver | Ketra Ecosense Ametrix | #G2-12-04-A-T-WFL-1-A-W-MOD JUMPER CABLES-120V-N3-IND-1-REC-BK | White | 1 | 11/LF | LED (3000K) |  | 11/LF | 120 | • GC to coordinate with architectural details • Fixture is dimmable. • Fixture is continuous using lengths as required to fill entire cove length to within 3"-6" of end. Provide longer jumper cables as required due to curvature of cove • Provide all necessary components for a fully functioning system • Provide for fixture commissioning
FC1 | Servery | Surface mounted, adjustable, continuous 3000K LED strip with approximately 900 fixture lumens per l.f. grazing optics, matte black cuttoff louver, ELV Reverse Phase dimming driver in architectural cove | Ecosense Ketra | #L50-I-12/48-12-30-80-MULT-TBD-LOUVER | Black | 1 | 12/LF | LED (3000K) |  | 12/LF | 277 | • GC to coordinate with architectural details • Fixture is continuous using lengths as required to fill architectural pocket to within 3"-6" of end. Center fixture run on opening. • Provide all necessary components for a fully functioning system • Fixture is dimmable. Refer to plans for control intent
FC2 | Typical floor corridors, Surgeons' Lounge, Servery, Boardroom, Main Lobbies, Concourse, Meditation Room, ICU Waiting Corridor | Surface mounted, nominal 2"w x 2-1/2"h continuous, adjustable 3000K warm white LED strip with flood distribution, approximatgely 700 lumens per l.f., with remote power supply and 0-10V dimming driver | Ketra Ecosense Ametrix | #G2-12-07-A-T-WFL-1-A-W-277V-N3-IND-1-REC-BK | White | 1 | 19/LF | LED (3000K) |  | 19/LF | 277 | • GC to coordinate with architectural details • Fixture is continuous using lengths as required to fill entire cove length to within 3"-6" of end. • Fixture is dimmable. Refer to plans for control intent • Provide all necessary components for a fully functioning system • Provide for fixture commissioning
FC3 | Conference Center, Lobby coves | Cove mounted, continuous, indirect asymmetric 3000K warm white LED with 1000 output lumens per foot; specular reflector; white steel housing and 0-10V dimming driver | Litecontrol Finelite | #15L-CC-AI-08-C1-30K-L100-D10-UNV-HPR-AMA-WKC | White | 1 | 16/LF | LED (3000K) |  | 16/LF | 277 | • GC to coordinate with architectural details • Fixture is continuous using lengths as required to fill entire cove length to within 3"-6" of end. Center fixture run within overall cove length. • Fixture is dimmable. Refer to plans for control intent
FD | General | Recesssed, nominal 4" diameter aperture x 7"d, downlight with 3000K LED, approximately 1300 fixture lumens specular clear reflector, white overlap flange and 0-10V dimming driver | Portfolio Lightolier Kurt Versen Edison Price Gotham | #LD4A-13-DE010-ERM4A13-8-30-4LM1-L1-WF | White | 1 | 22 | LED (3000K) |  | 22 | 120-277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FDA | ISO Rooms | Recesse, nominal 6" diameter aperture x 9"d, sealed, 3000K LED downlight with approximately 1500 delivered lumens; 90CRI; flush prismatic acrylic lens; anti-microbial paint; white overlap flange and integral 0-10 dimming driver | Portfolio Kirlin Kenall | #FFL6DA-15-DE010-FERM6A-15-9-30-FV/S6LMO-LI-FSBT6-PRISMATIC ACRYLIC LENS | White | 1 | 23 | LED (3000K) |  | 23 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD1 | Patient Rooms, Dining, Physician's Lounge, Sculpture niches; PACU | Recessed, pinhole aperture downlight with 3000K LED, approximately 160 fixture lumens, overlap flange; retrofit housing, dimmable to 10% with ELV driver | WAC Lightolier Sistemalux RSA | #HR-LED-211E-W-FINISH | Per Architect | 1 | 4 | LED (3000K) |  | 4 | 277 | • GC to coordinate with approved ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD1A | Gift Shop Entry | Recessed, pinhole aperture adjustable accent with 3000K LED, approximately 160 fixture lumens, overlap flange; retrofit housing, dimmable to 10% with ELV driver | WAC Lightolier Sistemalux RSA | #HR-LED-212E-W-FINISH | Per Architect | 1 | 4 | LED (3000K) |  | 4 | 277 | • GC to coordinate with approved ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD2 | Showers | Recesssed nominal 4" diameter x 9"d aperture wet location downlight with 3000K LED, approximately 900 fixture lumens, specular clear reflector; white overlap flange with gasket kit and integral 0-10V driver | Portfolio Lightolier Kurt Versen Edison Price | #LD4A-09-DE010-ERM4A09-8-30-4LM1-L1-WF-LGSKT4IP66 | White | 1 | 14 | LED (3000K) |  | 14 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD3 | Operating Rooms | Recessed, nominal 6" diameter aperture x 8"d, OR rated downlight with 4000K LED, approximately 3000 delivered lumens; 90CRI; flush prismatic acrylic lens; anti-microbial paint; white overlap flange and integral 1%, 0-10V dimming driver | Failsafe Kirlin Kenall | #FFL6DA/OR-30-DE010-FERM6A-30-9-40-FV/S6LMO-LI-FSBT6-89B1 | White | 1 | 46 | LED (4000K) |  | 46 | 120-277 | • Contractor to coordinate all mounting requirements with specified ceiling system • Fixture is dimmable. Refer to plans for control intent
FD4 | Scrub Alcove | Recessed, nominal 6" diameter aperture x 8"d, downlight with 3000K LED, approximately 1500 fixture lumens, 90CRI; regressed diffuse polycarbonate lens; anti-microbial paint; white overlap flange and integral 1%, 0-10V dimming driver | Failsafe Kirlin Kenall | #FL6DA-15-D010TE-FERM6A-15-8-30-FSR6LM1-W-WF | White | 1 | 23 | LED (3000K) |  | 23 | 120-277 | • Contractor to coordinate all mounting requirements with specified ceiling system • Fixtures shall be switched
FD5 | Lobbies | Recessed, nominal 4" x 9"d diameter aperture, adjustable accent with 3000K LED, approximately 1100 fixture lumens, narro distribution, specular clear reflector, white flange and 0-10V dimming driver | Kurt Versen | #F4949-WT-3000K-277 | White | 1 | 24 | LED (3000K) |  | 24 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent • PROVIDE FIXTURES TO AWARDED MANUFACTURER OF SERIES "FP9" FOR INTEGRATION INTO FIXTURE TYPES "FP9", "FP9A" & "FP9B". FOR YELLOW GOAT CONTACT: NICOLA CASALE #610-431-2512 OR CRAIG CORONA OF LUKAS LIGHTING #800-841-4011
FD6 | Not used
FD6A | Care Center | Semi-recessed decorative downlight with 3000K LED, approximately 1800 fixture lumens, crystal glass diffuser, retrofit housing and integral 0-10V dimming driver | Leucos | "Iside 2 LED" #30701141003499 | Crystal | 1 | 17 | LED (3000K) |  | 17 | 277 | • Fixture must be UL or ETL listed • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent •Final fixture selection shall be based on client's review of mock up
FD7 | Med Surge; Typical Patient Floor Waiting Area Corridor | Recessed, nominal 4-1/2" square aperture x 7"d downlight, with 3000K LED, approximately 1100 delivered lumens white splay trim and overlap flange, solite lens, integral power supply with 0-10V dimming driver | USAI Starfire Lighting Focal Point | #3110-B1-S-10-LSTD4-9012-C3-30KS-50-NC-277-DIML2 | Per Architect | 1 | 12 | LED (3000K) |  | 12 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD7A | Typical Patient Floor Consult Room | Similar to Type "FD7", except lensed wallwash version with approximately 1000 delivered lumens | USAI Starfire Lighting Focal Point | #3651-B1-10-LSTW4-6016-C3-30KS-W2-NC-277-DIML2 | White | 1 | 16 | LED (3000K) |  | 16 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD8 | VP Office | Similar to Type "FD", except wallwash version with kicker reflector | Portfolio Lightolier Kurt Versen Edison Price Gotham | #LD4A-1300-DE010-ERW4A13-8-30-4LW111-L1-WF | White | 1 | 22 | LED (3000K) |  | 22 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD9 | Conference Center, Prefunction, 1st Waiting Area, Surgery Waiting | Recessed, nominal 3" diameter aperture X 4"d downlight with 3000K LED, approximately 1100 delivered lumens, white angled trim and overlap flange, solite lens and integral 0-10V dimmable driver | USAI | #2221-B1-S-10-LRTD3-9020-M2-30KS-35-FT-277V-DIML2 | White | 1 | 20 | LED (3000K) |  | 20 | 120V in existing bldg; 277 in new | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer interface as required.
FD9A | Prefunction, 2nd fl corridor, 2nd Fl Elevator Lobby, Sculpture niches, Boardroom, | Recessed, nominal 3" diameter aperture x 8"d, adjustable accent, with 3000K 90CRI LED, approximately 1900 delivered lumens, frosted lens, white angled trim and overlap flange and integral 0-10V dimmable driver | USAI | #3231-B1-F-FINISH-AL30F-LRTA4-8433-C3-30KS-25-NC-277V-DIML2 | Per Architect | 1 | 33 | LED (3000K) |  | 33 | 277 | • Final fixture selection and placement shall be verified against artwork selection • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer interface as required.
FD9B | Boardroom | Recessed, nominal 3" diameter aperture x 4"d, lensed wallwasher, with 3000K LED, approximately 1100 delivered lumens, angled trim and integral 0-10V dimmable driver | USAI | #3751-B1-FINISH-LRTW4-6016-C3-30KS-W2-FT-277-DIML2 | Per Architect | 1 | 16 | LED (3000K) |  | 16 | 277 | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer interface as required.
FD10 | Boardroom | Recessed, pinhole aperture downlight with 3000K LED, approximately 160 fixture lumens, overlap flange; retrofit housing, dimmable to 10% with ELV driver | WAC Lightolier Sistemalux RSA | #HR-LED-211E-W-WT | Per Architect | 1 | 4 | LED (3000K) |  | 4 | 120 | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer interface as required.
FD11 | 2nd fl Concourse | Recessed nominal 5" diameter aperture x 10"d adjustable accent with 3000K LED, approximately 4900 delivered lumens, frosted lens, black regressed trim with overlap flange, integral 0-10V dimming driver. Optical accessories tbd | USAI | #6231-AB1-F-FINISH-LRTA6-8460-C2-30KS-20-NC1-277-DIML2-Accessories | Per Architect | 1 | 60 | LED (3000K) |  | 60 | 277 | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer interface as required.
FD12 | TAVR Rm, CT room | Recessed nominal 4" diameter aperture x 7"d, wet location downlight with 3000K LED, 1500 delivered lumens, white angled trim with overlap flange, solite lens and integral 1% Hi-Lume dimming driver | USAI | #3023-W-B1-S-10-LRTD4-9032-WGD1-3022KS-30-NC-277V-DIML4 | White | 1 | 32 | LED(3000K) |  | 32 | 120V in existing bldg; 277 in new | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture shall be dimmable to 1%
FD13 | TAVR Rm | Recessed nominal 4" diameter aperture x 7"d, wet location adjustable accent with 3000K LED, approximate 1700 delivered lumens, white angled trim with overlap flange, solite lens and integral 1% Hi-Lume dimming driver | USAI | #3233A30-W-B1-S-10-LRTA4-8432-WGD1-3022KH-30-NC-277V-DIML4 | White | 1 | 32 | LED(3000K) |  | 32 | 120V in existing bldg; 277 in new | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture shall be dimmable to 1%
FD14 | TAVR Rm | Recessed nominal 3" diameter aperture X 6"d, wet location downlight with 4000K LED; approximately 850 delivered lumens, gasket kit; white trim; retrofit housing; ingtegral power supply with 1% Hi-Lume dimming driver | USAI | #2221RT-W-B1-S-10-LRTD3-9014-M2-40KS-25-RT-277V-DIML4 | White | 1 | 14 | LED (4000K) |  | 14 | 120V in existing bldg; 277 in new | • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture shall be dimmable to 1%
FD15 | Care Center, Servery Entrance, Surgery Waiting, Typ Patient Floor Waiting | Recessed nominal 4-1/2" square aperture x 4"d 3000K LED downlight, approximately 1450 delivered lumens with splay trim, overlap flange, solite lens, integral power supply with 0-10V dimming driver | USAI Starfire Lighting Focal Point | #3311-B1-S-FINISH-LSLD4-9016-C3-30KS-25-FT-277-DIML2-MLXX IF REQUIRED | Per Architect | 1 | 16 | LED(3000K) |  | 16 | 120V in existing bldg; 277 in new | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent • Trim finish color to be confirmed via client's review of mock-up
FD15A | CCU Waiting | Recessed nominal 4-1/2" square aperture x 4"d 3000K LED downlight, approximately 2600 delivered lumens with solite lens, splay trim, overlap flange, integral power supply with 0-10V dimming driver | USAI Starfire Lighting Focal Point | #3110-B1-S-FINISH-LSTD4-9033-C3-30KS-25-NC-277-DIML2 | Per Architect | 1 | 33 | LED(3000K) |  | 33 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD15B | CCU Waiting | Recessed nominal 4-1/2" square aperture x 4"d 3000K LED adjustable accent, approximately 1450 delivered lumens with solite lens, splay trim, overlap flange, integral power supply with 0-10V dimming driver | USAI Starfire Lighting Focal Point | #3131-B1-S-FINISH-LSTA4-8416-C3-30KS-25-NC-277-DIML2 | Per Architect | 1 | 16 | LED(3000K) |  | 16 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD15C | CCU Waiting | Recessed nominal 4-1/2" square aperture x 4"d 3000K LED adjustable accent, approximately 2300 delivered lumens with solite lens, splay trim, overlap flange, integral power supply with 0-10V dimming driver | USAI Starfire Lighting Focal Point | #3131-B1-S-FINISH-LSTA4-8433-C3-30KS-25-NC-277-DIML2 | Per Architect | 1 | 33 | LED(3000K) |  | 33 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD16 | Loading Dock, Parking Garage Entry | Recessed, nominal 8" diameter aperture x 9"d downlight with 3000K LED, 8,000 fixture lumens, specular clear reflector, white overlap flange, gasket kit and on board power supply with 0-10V dimming driver | Portfolio Philips Acuity Brands | #LD8A-80-2-D010TE-ER8A-80-8-30-8LW1-LI-WF-LGSKT8IP65 | White | 1 | 96 | LED(3000K) |  | 96 | 277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FD17 | ED Lobby (Travertine Wall) | Similar to Type FD9A, except with narrow distribution optics and 90CRI | USAI | #3231-B1-N-FINISH-LRTA4-8433-C2-30KH-10-NC-277V-DIML2 | Per Architect | 1 | 33 | LED (3000K) |  | 33 | 277 | • Final fixture selection and placement shall be verified against artwork selection • Contractor shall coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer interface as required.
FM | MRI Rooms | Surface mounted, nominal 1"h x 1-1/4"w continuous, 3000K warm white, dimmable LED cove light with frosted acrylic lens. Provide MRI filter & manufacturer's dimmer kit. 0-10V dimming driver | Everbrite Lighting | #MALS-PER PLANS-MRI-SAFE-D-MCL-3000K-LENGTHS AS REQ'D-Dimmer Kit ECL-53-CR |  | 1 | 3/LF | LED(3000K) |  | 3/LF | 24VDC | •Refer to Architect's details • Remote power supply located per manufacturer's recommendations • Provide all necessary components for a fully functioning system •Run fixtures continuously, using lengths as required for extent of cove to within 3"-6" of ends.
FM1 | MRI Rooms | Recessed nominal 4" diameter aperture x 6"d non-ferrous downlight with 3000K LED with clear acrylic lens, semi-specular reflector, white overlap flange and 0-10V driver (B.O.) | Kenall Kirlin Eaton | #MRIRDL4-14L30K-MRIRRDL4L-24VDC-ALG-CSS-T | White | 1 | 14 | LED(3000K) |  | 14 | 24VDC | • Contractor to coordinate all mounting requirements with specified ceiling system. • Provide all necessary components for a fully functioning system • Fixture is dimmable. Refer to plans for control intent
FO | Operating Rooms | Recessed, 3-circuit, 2' x 4' x 6"d fixture with 4000K LED; green filter on outboard lighting zones; symmetric & asymmetric distribution, acrylic lens, integral 0-10V dimming driver; aluminum housing, with antimicrobial paint finish, gasket kit, with integral EM pack | FAILSAFE KENALL | #ORM-F-24-4-LD3-6-STD-40-277-ASY/SYM/RFI-ED-3C-EBP-AM-GRNF | White | 1 | 155 | LED(4000K) |  | 155 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer switch.
FO1 | Operating Rooms | Similar to Type "FO", except 2' x 2' version | FAILSAFE KENALL | #ORM-F-24-2-LD3-6-STD-40-277-ASY/SYM/RFI-ED-3C-EBP-AM-GRNF | White | 1 | 87 | LED(4000K) |  | 87 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system. • Fixture is dimmable, coordinate with appropriate dimmer switch.
FP | Dining Room | Cable mounted decorative pendant with nominal 20" diameter shade, retrofit LED lamp. | Tom Dixon | Beat Stout | Gray | 1 | Allow 60w | Brio A19 9W Warm eq by Solais |  | Allow 60w | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP1 | Servery Corridor | Decorative pendant with nominal 30" diameter x oa 8-1/4"d white shades, 3000K LED, 2400 fixtue lumens, integral driver | AFX | CZF-30-24-L-30-D1-FINISH-WHWH | Per Architect | 120 | 24 | LED(3000K) |  | 24 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP2 | Dining Room | Cable mounted decorative pendant with nominal 9" diameter x 12"h shade, retrofit LED lamp. | Tom Dixon | Beat Fat | Gray | 1 | 60 | Brio A19 9W Warm eq by Solais |  | 60 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP3 | Patient Floor Nurse Alcove | Monopoint mounted decorative pendant with white diffuse with blue interior, retrofit MR16 LED lamp and round canopy with 277/12 transformer. | LBL Lighting | #HS860-WHBU-SC-LED930-FSJ- & separate canopy 277transformer #CK001I-FJ-FINISH-LED-277 | White/Blue | 1 | 8 | LED(3000K) |  | 8 | 277/12 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at 6'-0" aff as confirmed via mock up
FP4 | Surgery Waiting; Public Waiting | Decorative pendant with 36" diameter x 12"h outer diffuser, 32" diameter x 9"h inner white diffuser with top and bottom white acrylic lens, with (3) LED lamps, 6" stem | Lumetta | #P2034-D929-LTC4-LBA4-LED-277-36" diam x 12" OAH diffuser-CSF6-6" Stem-3000K | Per Architect | 3 | 18.5 | LED(3000K) |  | 56 | 120V in existing bldg; 277 in new | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP5 | 2nd fl Lobby Concourse | Stem mounted decorative pendant with nominal 29"h x 17"diameter acrylic diffuser with metallic accents, flat canopy, modified stem lengths of 4', 5' & 6', 3000K LED, integral 0-10V driver | Winona | #WFP5430-12-LCP3A-SNFL-30K-MVOLT-LENS-FINISH-MOD-SINGLE PIECE STEM-4'-5'-6'LENGTHS | Per Architect | 1 | 67 | LED(3000K) |  | 67 | 120-277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. •Fixtures are mounted in groups of 3 (1 of each stem length)
FP6 | Physician's Lounge | Decorative pendant with 8' x 14"w x 12" outer diffuser, 7' x 11" x 9" inner diffuser, inner white diffuser with top and bottom white acrylic lens, 6'long canopy, (4) LED lamps, 15" stem | Lumetta | P2095-D929-LED-277-8' x 11" OA diffuser-STM 15"-LBA5-3000K | Per Architect | 4 | 16.8 | LED(3000K) |  | 68 | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP7 | Physician's Lounge (Above Lounge Seating) | Decorative pendant with 5" diameter globe diffuser with (1) LED lamp | Acclaim Lighting | "Phoenix" #TP6300-1-5" GLOBE-MED BASE LED RETROFIT LAMP | Clear acrylic/Silver | 1 | allow 35 | Brio A19 9W Warm eq by Solais |  | allow 35 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixtures at xx'-0" aff as confirmed by Architect
FP7A | Physician's Lounge (Above Tables) | Decorative pendant with 10" diameter globe diffuser with (1) LED lamp | Acclaim Lighting | "Phoenix" #TP6300-1-10" GLOBE-MED BASE LED RETROFIT LAMP | Clear acrylic/Silver | 1 | allow 35 | Brio A19 9W Warm eq by Solais |  | allow 35 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP8 | Retail | Decorative pendant with nominal 27" diameter x 3-3/4"h canopy with (24) cable mounted polished chrome & clear glass globes shades of varying dimensions and mounitng heights, integral 3000K LED and (3) 12VAC transformers in canopy, dimmable with ELV | Sonneman | "Grapes" #2918.01-AST | Per Architect | 1 | 100 | LED(3000K) |  | 100 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP9 | Main Lobby | Custom decorative light sculpture spanning approximately 26'L x 8' x 6' comprised of 72 suspended curved aluminum tubes and flatbar, suspended via cables from 26' x 8' polished aluminum canopy. 54 elements shall be illuminate via LED. Remote mount power supply in an accessible, ventilated location per manufacturer's instructions. | Yellow Goat Lukas Lighting | "Breaching" | Per Architect | 54 | allow 100 | LED(3000K) |  | allow 100 | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Contractor to take note of overall fixture weight and coordinate any required reinforcing members with structural engineer • 1/4" threaded rod provided by GC - verify quantity with manufacturer • Mount bottom of fixture at xx'-0" aff as confirmed by Architect • PROVIDE SEPARATE LINE ITEM PRICE FOR MANUFACTURER TO OVERSEE AND ADVISE INSTALLATION
FP9A | ED Lobby | Custom decorative light sculpture spanning approximately 12'L x 16' x 6' comprised of 46 suspended curved aluminum tubes and flatbar, suspended via cables from 12' x 16' polished aluminum canopy. 69 elements shall be illuminate via LED. Remote mount power supply in an accessible, ventilated location per manufacturer's instructions | Yellow Goat Lukas Lighting | "Breaching" | Per Architect | 69 | allow 100 | LED(3000K) |  | allow 100 | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Contractor to take note of overall fixture weight and coordinate any required reinforcing members with structural engineer • 1/4" threaded rod provided by GC - verify quantity with manufacturer • Mount bottom of fixture at xx'-0" aff as confirmed by Architect • PROVIDE SEPARATE LINE ITEM PRICE FOR MANUFACTURER TO OVERSEE AND ADVISE INSTALLATION
FP9B | CCU Waiting | Custom decorative light sculpture spanning approximately 10'L x 18' x 6' comprised of 43 suspended curved aluminum tubes and flatbar, suspended via cables from 10' x 18' polished aluminum canopy. 34 elements shall be illuminate via LED. Remote mount power supply in an accessible, ventilated location per manufacturer's instructions | Yellow Goat Lukas Lighting | "Breaching" | Per Architect | 34 | allow 100 | LED(3000K) |  | allow 100 | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Contractor to take note of overall fixture weight and coordinate any required reinforcing members with structural engineer • 1/4" threaded rod provided by GC - verify quantity with manufacturer • Mount bottom of fixture at xx'-0" aff as confirmed by Architect • PROVIDE SEPARATE LINE ITEM PRICE FOR MANUFACTURER TO OVERSEE AND ADVISE INSTALLATION
FP10 | Central Monitor | Cable mounted nominal 4"w x 2-1/4"h x 4' long indirect/direct pendant with 3000K LED, white cold rolled steel housing; integral power supply with 0-10V dimming driver. | Ledalite Neoray Peerless | #7505-LED-C-C-Q-N-04-1-2-E-W | White | 1 | 47 | LED(3000K) |  | 47 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount bottom of fixture at 7'-6" aff
FP11 | MD Lounge | Decorative pendant with 10" diameter globe diffuser with (1) LED lamp | Acclaim Lighting | "Phoenix" #TP6300-1-10" GLOBE-MED BASE LED RETROFIT LAMP | Clear acrylic/Silver | 1 | allow 35 | Brio A19 9W Warm eq by Solais |  | allow 35 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Mount bottom of fixture at xx'-0" aff as confirmed by Architect
FP12 | Surgery Waiting | Decorative pendant with 6" diameter x 18"h outer diffuser, 5" diameter x 10"h inner white diffuser with bottom white acrylic lens, with (1) LED lamp, 12" stem | Lumetta Lukas Lighting | #P2091-D929-LBA2-LED-277-6" diam x 18" OAH diffuser-CSF6-12" Stem-3000K | Per Architect | 1 | 18.5 | LED(3000K) |  | 18.5 | 120V in existing bldg; 277 in new | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware.
FP13 | Dining Room | Decorative pendant with 36" diameter x 12"h outer diffuser, 32" diameter x 9"h inner white diffuser with top and bottom white acrylic lens, with (3) LED lamps, 6" stem | Lumetta Lukas Lighting | #P2034-D921-LTC4-LBA4-LED-277-36" diam x 12" OAH diffuser-CSF6-6" Stem-3000K | Per Architect | 3 | 18.5 | LED(3000K) |  | 56 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount as per architect's elevations or as directed by Architect in field
FP14 | Main Lobby Seating Area | Decorative pendant with 30" diameter x 16"h outer diffuser, 26" diameter x 14"h inner white diffuser with top and bottom white acrylic lens, with (3) LED lamps, 18" stem | Lumetta Lukas Lighting | #P2034-D925-LTC4-LBA4-LED-277-30" X 16" OAH diffuser-CSF6-18" Stem-3000K | Per Architect | 3 | 18.5 | LED(3000K) |  | 56 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount as per architect's elevations or as directed by Architect in field
FP15 | 1st & 2nd Fl Elevator Lobbies | Decorative pendant with 18" diameter x 16"h outer diffuser, 14" diameter x 14"h inner white diffuser with bottom white acrylic lens, with (1) LED lamp, 24" stem | Lumetta Lukas Lighting | #P2092-D921-LBA2-LED-277-18" X 16" OAH diffuser-CSF6-24" Stem-3000K | Per Architect | 1 | 18.5 | LED(3000K) |  | 18.5 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount as per architect's elevations or as directed by Architect in field
FP16 | 1st & 2nd Fl Elevator Lobbies | Decorative pendant with 24" diameter x 16"h outer diffuser, 20" diameter x 14"h inner white diffuser with bottom white acrylic lens, with (1) LED lamp, 20" stem | Lumetta Lukas Lighting | #P2023-D921-LBA3-LED-277-24" X 16" OAH diffuser-CSF6-20" Stem-3000K | Per Architect | 1 | 18.5 | LED(3000K) |  | 18.5 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount as per architect's elevations or as directed by Architect in field
FP17 | 1st & 2nd Fl Elevator Lobbies | Decorative pendant with 30" diameter x 16"h outer diffuser, 26" diameter x 14"h inner white diffuser with top and bottom white acrylic lens, with (3) LED lamps, 16" stem | Lumetta Lukas Lighting | #P2034-D921-LTC4-LBA4-LED-277-30" X 16" OAH diffuser-CSF6-16" Stem-3000K | Per Architect | 3 | 18.5 | LED(3000K) |  | 56 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount as per architect's elevations or as directed by Architect in field
FP18 | CCU Patient Elevators | Decorative pendant with 30" diameter x 12"h outer diffuser, 26" diameter x 11"h inner white diffuser with top and bottom white acrylic lens, with (3) LED lamps, 4" stem | Lumetta Lukas Lighting | #P2034-D932-LTC4-LBA4-LED-277-36" diam x 12" OAH diffuser-CSF6-4" Stem-3000K | Per Architect | 3 | 18.5 | LED(3000K) |  | 56 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount as per architect's elevations or as directed by Architect in field
FP19 | Admin Waiting | Cable mounted, nominal 3"w x 4"hx 8' long direct pendant with 3000K LED, approximately 360 lumens per l.f.; extruded aluminum housing, bottom diffusing acrylic lens and integral 0-10V dimming driver. Provide custom color on canopy | Pinnacle Selux Finelite Prudential | #EX33-A-N-30-8-AC48JB-277-1D-FINISH-CC-C | Per Architect | 1 | 6/LF | LED(3000K) |  | 6/LF | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system including necessary hardware. • Mount bottom of fixture to align with bottom of wood slat ceiling members
FR | Waiting, B1 Corridor, Admin., Care Center, Vestibule, Multidisciplinary Team Work Room, Surgery Waiting, Conference Room | Recessed, nominal 4"w x 8"d continuous linear slot with 3000K LED, approximately 850 delivered lumens per l.f., regressed acrylic diffusing lens; white extruded aluminum trim and integral 0-10V dimming driver. Fixture resides in both gwb & atc. Provide overlap flange on fixtures in GWB | Starfire Lighting Prudential Neoray Finelite | #VR4-LP8-30-H-ST-PER PLANS-X/P-W-2 | White | 1 | 8/LF | LED (3000K) |  | 8/LF | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FR1 | Main Lobby, Concourse | Recessed, nominal 15"l x 1"w 7"d linear high powered downlight with 3000K LED, medium beam distribution dimmable with remote 0-10V dimming driver. Provide trimless in Concourse. | Iguzzini | I.MK56/I.MK43-REM-01/02-BI5117/BI5118-4444-0700-034-UNV-D10 | Trimless = Black Trim= White | 1 | 36.5 | LED (3000K) |  | 36.5 | 277 | • Note to GC - fixture housing has a large footprint • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FR2 | Corridors, Bathrooms, Board room, Surgeon's Lounge, Physician's Lounge, Servery, MD Lounge | Perimeter mount, nominal 4" aperture x 7"d continuous slot with 3000K LED, approximately 950 lumens per l.f.; , "control deflector" to mask direct view of diodes, white steel housing; integral 0-10v dimming driver. Provide corners as per plans, end caps and straight extension segments as required for a clean installation. Fixture is adjacent to ATC | Litecontrol Prudential | #WS-L60-PER PLANS-D950-30K-CWM-G-D10-277LCD WS-L60-G-LCD-EC/SE/IC/OC-CWM AS REQ'D. | White | 1 | 16/LF | LED (3000K) |  | 16/LF | 120V in existing bldg; 277 in new | • Fixtures shall run continuously for length of corridor, per plans, including corners. • Contractor shall coordinate all mounting reqirements with specified ceiling system. • Refer to architect's details
FR2A | Care Center; Public Elevator Lobby Gift Shop | Perimeter mount, nominal 4" aperture x 7"d continuous slot with 3000K LED, approximately 950 lumens per l.f.; , "control deflector" to mask direct view of diodes, white steel housing; integral 0-10v dimming driver. Provide end caps and straight extension segments as required for a clean installation. Fixture is installed in GWB | Litecontrol Prudential | #WS-L60-PER PLANS-D950-30K-CWM-DP-D10-277-LCD WS-L60-DP-LCD-EC/SE AS REQ'D-CWM | White | 1 | 16/LF | LED (3000K) |  | 16/LF | 277 | • Fixtures shall run continuously as shown per plans. • Contractor shall coordinate all mounting reqirements with specified ceiling system. • Refer to architect's details
FR2B | Patient Bathroom | Perimeter mount, nominal 4" aperture x 7"d continuous slot with 3000K LED, approximately 650 lumens per l.f.; , "control deflector" to mask direct view of diodes, white steel housing; integral 0-10v dimming driver. Provide end caps as required for a clean installation. Fixture is installed in GWB | Litecontrol Prudential | #WS-L60-PER PLANS-D065-30K-CWM-DP-D10-277-LCD WS-L60-DP-LCD-EC AS REQ'D-CWM | White | 1 | 10.5/LF | LED (3000K) |  | 10.5/LF | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture selection & color temperature to be confirmed via mockup
FR3 | Patient Floor Corridors | Perimeter mount, nominal 9" aperture X 10-1/2"d, continuous lightslot with 3000K LED, approximately 800 lumens per l.f.; white steel housing; integral 0-10v dimming driver | Litecontrol Prudential | #L20-PER PLANS-D080-30K-CWM-D10-1CWQ-277-L20-EC-SE-CWM | White | 1 | 13/LF | LED (3000K) |  | 13/LF | 120V in existing bldg; 277 in new | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FR4 | Conference Center | Recessed, nominal 4"w, continuous linear slot with 3000K LED, approximately 1000 fixture lumens per l.f., regressed acrylic diffusing lens; white extruded trim with overlap flange and integral 0-10V dimming driver | Starfire Lighting Prudential Neoray Finelite | #VR4-LP8-30-H-ST-PER PLANS-F-W-2 | White | 1 | 8/LF | LED (3000K) |  | 8/LF | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FR4A | Care Center, Admin | Similar to Type "FR4", except with 1100 lumens per LF, trimless in atc | Starfire Lighting Prudential Neoray Finelite | #VR4-LP8-30-C 1100LMS/LF-ST-PER PLANS-X-W-2 | White | 1 | 8.7/LF | LED (3000K) |  | 8.7/LF | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FR4B | C Suite Offices | Similar to Type "FR4", except in atc with matte black louver below lens | Starfire Lighting Prudential Neoray Finelite | #VR4-LP8-30-H-ST-PER PLANS-X-W-2-LOUVER | White | 1 | 8/LF | LED (3000K) |  | 8/LF | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Provide appropriate switch
FR5 | Not used
FR6 | Gift Shop | Recessed, continuous extruded channel with (1) circuit track, fully adjustable track heads @ 3' oc with hexcell louver and solite lens with mitered corners in ATC. All interior components shall be matte black. Refer to plans for configuration | LF Illumination RSA Litelab | #EF450 SYSTEM W/ EF-408 HEADS W/-HEX LOUVER-SOLITE LENS | Per Architect |  | allow 8w/LF | LED (3000K) |  | allow 8w/LF | UNV | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent • Factory generated shop drawing required for review and approval
FR7 | Gift Shop | Recessed, continuous extruded channel with (1) circuit track, fully adjustable track heads @ 2' oc with hexcell louver and solite lens in wood ceiling. All interior components shall be matte black. Refer to plans for run lengths | LF Illumination RSA Litelab | #EF450 SYSTEM W/ EF-408 HEADS W/-HEX LOUVER-SOLITE LENS | Per Architect |  | allow 8w/LF | LED (3000K) |  | allow 8w/LF | UNV | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent • Factory generated shop drawing required for review and approval
FS | Overheads/ Millwork | Surface mounted, nominal 1-1/2"h x 6"d, continuous tasklight with 3000K LED, anti-microbial paint; acrylic prismatic lens; white steel housing with rocker switch | Failsafe Mercury Starfire Lighting | #UCL-LENGTH-LD4-30-A12125-EDC1-UNV-RSW-AM | White | 1 | 7/lf | LED (3000K) |  | 7/lf | UNV | • Fixture shall be hardwired • Provide fixture lengths as required to run end to end to fill overhead or millwork length. Center entire run within overhead with max. 6" space at either end. • In continuous runs, provide rocker switch for first fixture in line, this controls entire run. Fixtures downstream do not have rocker switches • Coordinate lip dimensions on overhead to mask view of fixture • Fixture shall be fed from back, not sides. No exposed wiring will be accepted
FS1 | Public Bathrooms | Wall mounted nominal 22"l x 5"w x 2"d sconce with 3000K LED, glass accents and satin nickel finish | Tech Lighting | "Arim" #700WSARM-L-S-C-S-LED/LED277 | Satin Nickel | 1 | 25 | LED (3000K) |  | 25 | 120V in existing bldg; 277 in new | • GC to coordinate all mounting requirements. • Mount at height & orientation as shown on Architect's elevations or as directed by Architect in field • Provide blocking as required • Fixture shall be switched
FS3 | C Suite Offices, PACU, Pre/Post Recovery | Surface mounted,nominal 7"d x 2-1/2"h x 4' OR 8' long indirect/direct with 3000K LED,approximately 857 fixture lumens per l.f., steel housing with straight end capr and partial perf bottom and integral 0-10V dimming driver | Corelite | IW-S-P-2-4-L30-1-D-277-SU-WA-4/8-STD-FINISH-ES | Per Architect | 1 | 8.25/LF | LED (3000K) |  | 8.25/LF | UNV | • GC to coordinate all mounting requirements. • Mount at height as shown on Architect's elevations or as directed by Architect • Provide blocking as required • Fixture shall be dimmed
FS4A | Stairs | Wall mounted, nominal 4" x 4" x 4'L direct LED strip with white extruded aluminum housing; acrylic high transmission lens, dust cover on indirect component, integral 0-10V driver with occ sensor | Neoray Focal Point Pinnacle Finelite | #S23-D-W-2-L30-SR-4-2-DD-SI-S93HTS-W-4-OCC SENSOR | White | 1 | 37 | LED (3000K) |  | 37 | UNV | • GC to coordinate all mounting requirements. • Mount at height as shown in model • Provide blocking as required • Fixture is dimmable. Refer to plans for control intent
FS5 | Iso Rooms/Ante room, Soiled Workrooms | Surface mounted, nominal 2"h x76"d, continuous tasklight with 3000K LED, anti-microbial paint; acrylic prismatic lens; gasket, white steel housing | Failsafe Kenall Healthcare Lighting | #UCLV-LENGTH-LD4-30-A12125-EDC1-UNV-AM-GSK-1P63 | White | 1 | 7/lf | LED (3000K) |  | 7/lf | UNV | • Provide fixture lengths as required to run end to end to fill overhead or millwork length. Center entire run within overhead with max. 6" space at either end. • Hardwire to wall switch
FS6 | Steam Sterilization | Surface mounted 4' long explosion proof LED fixture with integral electronic driver; aluminum components; glass lens and surface mounting kit | LDPI | #380-LED-H-4-2L-4-UNV1-P | White | 1 | 37 | LED (4000K) |  | 37 | UNV | • Contractor to coordinate all required accessories for complete installation per manufacturer's recommendations •Fixture shall be switched
FS7 | MRI, C/T, Radiology | Wall or ceiling mounted single face red LED indicator sign with rectangular mounting canopy and nominal 14"l x 10"h x 3-1/2"d polycarbonate housing | Kenall Kirlin Healthcare Lighting | #METMSU-MW-R-XIU/MIU/IU-DT | White | 1 | Approx 2W | LED |  | Approx 2W | 120-277 | • Architect to confirm text for each location • GC to coordinate all mounting requirements. • Mount at height as shown on Architect's elevations or as directed by Architect • Fixture is activated by machines. GC to verify
FS8 | Bereavement | Wall mounted, nominal 4-1/2"d X 5"h X 4' or 8' L indirect with 3000K LED, 675 fixture lumens per l.f., extruded aluminum housing, on board 0-10 dimming driver. Clear lens on top of fixture | Neoray Pinnacle Selux | S23-I-W-2-L30-4/8-277-DD-S92HTS-CLEAR TOP LENS | White | 1 | 11/lf | LED (3000K) |  | 11/lf | 277 | • GC to coordinate all mounting requirements. • Mount at height as shown on Architect's elevations or as directed by Architect • Provide blocking as required • Fixture shall be dimmed
FS9 & FS10 | Not Used
FS11 | OR Clean Corridors | Surface mounted, nominal 8-1/2" x 8-1/2" x 2' or 4'l, wet location troffer with 3000K LED, white steel housing, prismatic acrylic angled lens and integral electronic driver | Failsafe Certolux Kenall | FCC-S-2/4-LD4-1-LO-30-277-80-84-EDC-1-SSP-WL | White | 1 | 26/4lf | LED (3000K) |  | 26/4lf | 277 | • GC to coordinate all mounting requirements. • Mount as shown on Architect's details • Use 2' & 4' fixture lengths as needed to fill lenth of architectural regress. Fixtures run continuously
FS12 | CCU Nurse alcove, Patient Rooms | Wall recessed nominal 4-1/2"h x 2-1/2"w LED wet location area light with white finish and integral non-dimmng driver | CSL ACDC | #SS3008-WT-MOD 3000K Galaxy | White | 1 | 2.5 | LED (3000K) |  | 2.5 | 120 | • GC to coordinate all mounting requirements. • Mount at height as shown on Architect's elevations or as directed by Architect • Final fixture selection shall be based on client's review of Mock-Up
FS13 | CCU Patient Room | Wall mounted LED sconce with white diffuser; chrome finish on all exposed metal and integral 0-10V dimming driver | Eureka | FOLIA' #3216-LED.11.30-277V-DV | White | 1 | 11 | LED (3000K) |  | 11 | 277 | • GC to coordinate all mounting requirements. • Mount at height as shown on Architect's elevations or as directed by Architect • Final fixture selection shall be based on client's review of Mock-Up
FS14 | Clean Dock, Soiled Dock, 3rd Fl Med Gas Room | Surface mounted 8" outer diameter x nominal 13"h LED cylinder with 3000K LED, approximately 4500 output lumens, specular reflector; integral power supply with 0-10v driver and exterior finish as per architect | Gotham | #EVO-CYL-30/45-6AR-MWD-LS-277-EZ1-FCM-FINISH | Per Architect | 1 | 47 | LED (3000K) |  | 47 | 277 | • GC to coordinate all mounting requirements. • Mount to underside of ceiling
FS15 | Loading Dock | Wall mounted swing arm lamp with 5' long cordset, 60" arm; LED lamp, swivel head, yellow finish, | Lighting Specialties | #04881302 DKL LED37-60VA-LED | Safety Yellow | 1 | 37 | LED |  | 37 | 120 | • GC to coordinate all mounting requirements. • Mount at height as shown on Architect's elevations or as directed by Architect
FS16 | Dialysis | Decorative pendant with nominal 24" diameter x oa 8-1/4"d white shades, 3000K LED, 2400 fixtue lumens, integral driver | AFX | CZF-24-24-L-30-D1-FINISH-WHWH | Per Architect | 120 | 24 | LED (3000K) |  | 24 | 120 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system.
FS17 | Med Surge Care Center Desk base, Servery Island | Surface mounted nominal 1-1/2" x 1-1/2" adjustable 3000K LED strip in 6" & 12" lengths run continuously with approximately 250 fixture lumens per l.f. | Color Kinetics | eW Cove EC Powercore' #523-000090-83 & 523-000091-83 | White | 1 | 3.3/LF | LED (3000K) |  | 3.3/LF | 120V in existing bldg; 277 in new | •Provide all necessary components for a fully functioning system. • GC to coordinate all mounting requirements with Architect's details. • Fixture runs continuous in base of desk, use 6" & 12" lengths as necessary to fill millwork length
FS18 | 1st Floor Corridor | Wall mounted nominal 5"w x 3"d x 4'l direct/indirect sconce with flat extruded aluminum body, 3000K LED, 0-10V driver | Eureka | #3132-48-2XLED.22.30-277-DV-FINISH-3980 | Per Architect | 1 | allow 25w | LED (3000K) |  | allow 25w | 120 | • GC to coordinate all mounting requirements. • Provide blocking as required • Mount at height as shown on Architect's elevations or as directed by Architect • Final fixture selection based on Architect's review of sample
FT | Dining Room, Servery, Admin Waiting, Donor Wall, Meditation Room | Surface mounted track. Provide cable suspension accessory as required to align track heads FT1 with bottom of wood slat ceiling | WAC Litelab | #WHT-LENGTH-FINISH-WMST-X | Black, Donor Wall = Per Architect | n/a |  | n/a |  |  | 277 | • GC to coordinate all mounting requirements • Refer to Architect's details •Provide all necessary components for a fully functioning system.
FT1 | Dining Room, Servery | Track mounted 3000K LED accent head with frosted lens and honeycomb louver; | WAC Litelab | #WHK-LED512N30-BK-LENS-16-FR-LENS-HCL | Black | 1 | 11.5 | LED (3000K) |  | 11.5 | 277 | •Provide all necessary components for a fully functioning system. • GC to coordinate all mounting requirements with Architect's details. • Bottom of track head shall align with bottom of wood slats
FT2 | Admin Waiting, Donor Wall, Meditation Room | Track mounted 90CRI, 3000K LED accent head with spread lens | WAC Litelab | #WTK-LED512N-930-PT-LENS-16-SPR-PT | Silver | 1 | 11.5 | LED (3000K) |  | 11.5 | 277 | •Provide all necessary components for a fully functioning system. • GC to coordinate all mounting requirements with Architect's details.
FX | Elevator Pits | Wall mounted jelly jar with 4000K LED, frosted globe, aluminum cage and constant current driver. | RAB Eaton Acuity Brands | #VXBRLED26NDG-3/4 | Per Architect | 1 | 30 | LED (4000K) |  | 30 | 100V-277V | • GC to coordinate all mounting requirements.
FX1 | Exterior General, Parking Garage, Roof | Surface wall mounted; wet location 3000K LED area light with full cutoff; bottom glass lens; gasket; die-cast aluminum housing in finish as selected by Architect; constant current driver | RAB Lighting | #SLIM-18W-Y-FINISH | Per Architect | 1 | 18 | LED (3000K) |  | 18 | 277 | •Mount light fixture centered above door •Fixture shall be UL or ETL & wet location listed
FX2 | Exterior General, Parking Lot | Post mounted area light with 16' aluminum pole, 3000K LED, symmetric reflector, flat shade and integral 0-10V driver | Selux | #RRSL-1-RP16-L55-3000-BK-277-DM-MOUNTING | Black | 1 | 55 | LED (3000K) |  | 55 | 277 | • GC to coordinate all mounting requirements. • Provide all necessary components for a fully functioning system
FX3 | Exterior General, Parking Lot | Similar to type FX2, except with asymmetric distribution | Selux | #RRAL-1-RP16-L55-3000-BK-277-DM-MOUNTING | Black | 1 | 55 | LED (3000K) |  | 55 | 277 | • GC to coordinate all mounting requirements. • Provide all necessary components for a fully functioning system
FX3A | Exterior General, Parking Lot | Similar to Type "FX3", except with GFCI Receptable | Selux | #RRAL-1-RP16-L55-3000-BK-277-REC-DM | Black | 1 | 55 | LED (3000K) |  | 55 | 277 | • GC to coordinate all mounting requirements. • Provide all necessary components for a fully functioning system
FX4 | ED Ambulance drop-off | Similar to type "FX3", except wall mounted version | Selux | #RRAL-W-L55-3000-FINISH-277-DM | Per Architect | 1 | 55 | LED (3000K) |  | 55 | 277 | • GC to coordinate all mounting requirements. • Provide blocking as required • Provide all necessary components for a fully functioning system •Mount at height as shown on Architect's elevations or as directed by Architect
FX5 | Elliptical planters/benches | Surface mounted, nominal 3/4" x 3/4", continuous, wet location, curvable, glowing striplight with 3000K LED, mounting clips, remote 0-10V driver in manufacturer provided wet location enclosure | Optic Arts | FLEXNEON-F-30-24V-LENGTH-GG24-UNV-SLD-DIM1B (0-10V dimming driver) - WL box | White | 1 | 4/LF | LED (3000K) |  | 4/LF | 120-277 | • GC to coordinate all mounting requirements with planter design/details • Provide all necessary components for a fully functioning system • Manufacturer's shop drawing required for review and approval
FX6 | General | Wet location nominal 27"h x 4-1/2"w direct bollard with marine grade, extruded aluminum body, 3000K LED, gasketed enclosure, anchor base, integral 12V AC driver, remote magnetic transformer | Bega | #7263LED | Black | 1 | 5 | LED (3000K) |  | 5 | 12V-24V | • GC to coordinate all mounting requirements with paver design/details • Provide all necessary components for a fully functioning system
FX7 | American Flag | Ground mounted adjustable accent with 3000K LED, cylindrical housing with 45degree cutoff, soft focus lens, honeycomb louver, remote transformer with 0-10V dimming driver | BK Lighting Kim Lighting | K2-LED-X50-NFL-FINISH-12-11-A-HP2RM-HPD52-MT-GMR | Black | 1 | allow 52 | LED (3000K) |  | allow 52 | 120-277 | • GC to coordinate all mounting requirements with paver design/details • Provide all necessary components for a fully functioning system • Beam spread and accessories shall be coordinated with final flag dimensions
FX8 | Curved Feature Wall | Surface mounted, nominal 1.25" diameter x 6"L, adjustable, continuous 3500K LED with parabolic reflector in extruded acrylic housing with mounting clips. Distribution tbd based on mock up. remote mounted IP65 driver | Emerge Lighting | #CWE-6"-BEAM ANGLE TBD-35K-CABLES-0-10V-POWER SUPPLY |  | 1 | 4/LF | LED (3500K) |  | 4/LF | 24VDC | •Final fixture selection and color temperature shall be confirmed via mock-up • Provide all necessary components for a fully functioning system • Manufacturer's shop drawing required for review and approval
FX9 | Wall | Wall recessed, nominal 13"l x 5"h x 4"d area light with 3000K LED,matte black faceplate, asymmetric reflector, aluminum housing, integral 0-10V driver | Bega Winona WAC Lighting | #3065 LED | Black | 1 | 8.4 | LED (3000K) |  | 8.4 | 120-277 | • GC to coordinate all mounting requirements.
FX10 | Canopy | Recessed nominal 1-3/4"w x 2"dx 3'l linear with 3000K LED in manufacturer provide channel with matte black cutoff louver, remote power box woth 0-10V driver | i2 Systems | #V2355-A-3-3-CBB-O-B-LL-205-10V-685-02026-100-POWER BOX-VLA-9-BLACK LOUVER-CHANNEL | Black | 1 | 14/LF | LED (3000K) |  | 14/LF | 120-277 | • GC to coordinate all mounting requirements with ceiling panel manufacturer • Provide all necessary components for a fully functioning system
FX11 | Loading Dock | Wall arm mounted downlight with 3000K LED, approximately 1600 fixture lumens, nominal 11"d x 10"w x 2"h cutoff shield, aluminum housing, gasket kit, on 24" mounting arm, integral driver | RAB Lighting Hess Lighting Kim Lighting | WPLED18Y-FINISH-ARM-24-SV-FINISH-SWP1CFA | Per Architect | 1 | 18 | LED (3000K) |  | 18 | 277 | • GC to coordinate all mounting requirements. • Provide blocking as required •Mount light fixture centered above door
P1 | Parking Garage | Recessed nominal 2' diameter x 8"d, damp location, ambient area light with 3000K LED, convex diffusing lens, gasket kit, white steel housing painted after fabrication and integral 0-10V driver | Mark Lighting Focal Point | #MGL-LED-24IN-N-30-EZB-277-CCV-SM2–MOD DL/GSKT" | White | 1 | 34 | LED (3000K) |  | 34 | 277 | • Contractor shall coordinate all trim and mounting reqirements with specified ceiling system.
NOTES:
CONTRACTOR TO VERIFY FIXTURE FLANGE CONDITIONS WITH SELECTED CEILING SYSTEMS
CONTRACTOR TO COORDINATE ALL CABLES, CONNECTORS AND ACCESSORIES FOR COMPLETE INSTALLATION PER MANUFACTURER'S RECOMMENDATIONS
CONTRACTOR TO PROVIDE CONTINUOUS BLOCKING AS REQUIRED
CONTRACTOR TO CONFIRM SPECIFIED LAMP COLOR TEMPERATURE MATCHES EXISTING, AS REQUIRED
ALL LED FIXTURES SHALL BE DLC (DESIGN LIGHTING CONSORTIUM) OR ENERGY STAR CERTIFIED
** ALL LIGHT FIXTURES IN EXISTING BUILDINGS AND NEW BOILER PLANT SHALL BE 120V. REFER TO ELECTRICAL LIGHTING DRAWINGS.**

## Mercer
181 MERCER LIGHTING FIXTURE SCHEDULE - 100% CD
TYPE | LOCATION | DESCRIPTION | MANUFACTURER | CATALOG NUMBER | FINISH | LAMP DATA |  |  | Fixture Wattage | INPUT WATTS | VOLTS | NOTES
[6 empty] | NO. | WATTS | TYPE
EX1 | General | Single face, universal mount, edgelit LED emergency exit sign with high impact acrylic panel with nickel cadmium battery | Sure-Lite | #ELX7-1-70-00-FINISH-R-XX | Per Architect | 1 | 4.8 | LED |  | 4.8 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on Life Safety plans
EX2 | General | Double face, universal mount, edgelit LED emergency exit sign with high impact acrylic panel with nickel cadmium battery | Sure-Lite | #ELX7-2-70-00-FINISH-R-XX | Per Architect | 1 | 4.8 | LED |  | 4.8 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on Life Safety plans
EX3 | General | Single face, universal mount, AC, die-cast aluminum LED exit sign | Sure-Lite Prescolite Dualite | #CAX6-1-00-65-R-FINISH | Per Architect | 1 | 4 | LED |  | 4 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on Life Safety plans
EX4 | General | Double face, universal mount, AC, die-cast LED exit sign | Sure-Lite Prescolite Dualite | #CAX6-2-00-65-R-FINISH | Per Architect | 1 | 4 | LED |  | 4 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on Life Safety plans
EX5 | Roof | Weather proof LED exit sign | Surelite Prescolite Dualite | #UX6-0/1-95-R-FINISH | Per Architect | 1 | 4 | LED |  | 4 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on Life Safety plans
EX6 | Theater | Single face, recessed mount, die-cast aluminum, exit sign in powder coat bronze finish | Lithonia | #LRE-S BZ-1-R ELA ERK | Per Architect | 1 | 2 | LED |  | 2 | 120/277 | • Contractor to coordinate all mounting requirements • Provide with quantity of faces and chevrons as indicated on Life Safety plans
FB | BOH | Ceiling; wall or chain mounted nominal 3"W X 4"H X 4'L 3500K LED striplight with approximately 4100 fixture lumens, frosted lens with wide distribution, white steel housing and integral 0-10V dimming driver | Metalux Lithonia Mercury | #4SNLED-LD5-41SL-LW-UNV-L835-CD-1-AYC-CHAIN/SET AS REQ'D. | White | 1 | 34.6 | LED (3500K) |  | 34.6 | UNV | • Contractor shall coordinate all mounting reqirements with specified ceiling and/or wall system. • Provide chainset and/or wall mounting brackets as required • Fixture shall be switched • Mount bottom of fixture at 9'-0" AFF, UON • Refer to E-200 series plans for additional information regarding mounting heights
FB1 | BOH | Ceiling; wall or chain mounted nominal 3"W X 4"H X 2'L 3500K LED striplight with approximately 1800 fixture lumens, frosted lens with wide distribution, white steel housing and integral 0-10V dimming driver | Metalux Lithonia Mercury | #2SNLED-LD5-16SL-LW-UNV-L835-CD-1-AYC-CHAIN/SET AS REQ'D. | White | 1 | 15.9 | LED (3500K) |  | 15.9 | UNV | • Contractor shall coordinate all mounting reqirements with specified ceiling and/or wall system. • Provide chainset and/or wall mounting brackets as required • Fixture shall be switched • Mount bottom of fixture at 9'-0" AFF, UON • Refer to E-200 series plans for additional information regarding mounting heights
FB2 | Mechanical Room | Chain hung nominal 1' x 4' high-bay with 3500K LED, approximately 7,000 fixture lumens, wide distribution, frosted acrylic lens, white steel housing and integral 0-10V driver | Metalux Lithonia Columbia | #4ILED-LD5-7-W-FL-UNV-L835-CD-1-AYC-CHAIN/SET/U | White | 1 | 50 | LED (3500K) |  | 50 | 277 | • Contractor shall coordinate all mounting reqirements with specified ceiling system. • Fixture shall be switched • Refer to E-200 series plans for information regarding mounting heights
FB3 | BOH Dining, Café BOH | Recessed 2' x 2' ambient troffer, sealed and gasketed, with 3500K LED, approximately 6500 fixture lumens prismatic acrylic lens, white steel housing and integral 0-10V driver | Fail-Safe Metalux Columbia | CLM-24-2-INS-A12125-LD4- 4-STD-35-277-EDC-1 | White | 1 | 73.2 | LED (3500K) |  | 73.2 | 277 | • GC to coordinate fixture trim with specified ceiling system
FD | Circulation | Recessed, nominal 4" diameter aperture x 7"d, downlight with 3500K LED, approximately 1500 fixture lumens semi-specular clear reflector, white overlap flange and 0-10V dimming driver | Portfolio Lightolier Kurt Versen Edison Price Gotham | #LD4B-15-DE010-EU4B-1020-80-35-4LB-M-2-H | White | 1 | 15.5 | LED (3500K) |  | 15.5 | 120-277 | • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent
FS | Stairs | Wall mounted, direct/indirect 2-circuit, 4' long, 5000K LED strip with 800 lumen output per l.f.; extruded aluminum housing, satin acrylic lens, on board power supply with dimming driver and integral occupancy sensor | Axis | #SP16237 1-PWWLED-800-80-50-S-4-FINISH-UNV-DP-2-OS | Per Architect | 1 | 28.68 | LED (5000K) |  | 28.68 | 120-277 | • GC to coordinate all mounting requirements. • Mount at height as shown in model • Provide blocking as required • Fixture is dimmable. Refer to plans for control intent • 5000K is required to charge photoluminescent tape • Mount center of fixture at 8'-0" above landing or tread
FS1 | Elevator Pit, Holding | Surface, ceiling or wall mounted vandal resistant, wet location, nominal 5" x 5" x 4'l ambient strip with 3000K LED, approximately 3000 delivered lumens, wraparound prismatic lens, steel housing and integral constant current driver | Luminaire LED | #LVP524-25W-3500-120&277-CP-WHT-WET | White | 1 | 26.8 | LED (3500K) |  | 26.8 | UNV | • GC to coordinate all mounting requirements and provide wall mounting brackets as required. • Provide 120V in Elevator Pits, 277V in all other spaces | Elevator pits to be 120, Holding to be 277
FS2 | BOH | Surface or stem mounted downlight with 4" diameter x 11"h, white cylindrical aluminum housing; 3000K LED, 1500 fixture lumens, semi-specular clear reflector with medium distribution and 0-10V integral dimming driver | Portfolio Lightolier Gotham | #LSR4B-15-DE010-P-EC4B-1020-80-35-4LB-M-0-H-P834P | White | 1 | 15.5 | LED (3500K) |  | 15.5 | 120-277 | • Contractor to field cut and thread stem as required. • Contractor to coordinate all mounting requirements with specified ceiling system. • Fixture is dimmable. Refer to plans for control intent • Mount bottom of fixture at 9'-0" AFF, UON
FX | Roof | Surface wall mounted; wet location 3000K LED area light with full cutoff; bottom glass lens; gasket; die-cast aluminum housing in finish as selected by Architect; constant current driver and integral photocell | RAB Lighting | #SLIM-18W-Y-FINISH/PC2 | Per Architect | 1 | 18 | LED (3000K) |  | 21 | UNV | • GC to coordinate all mounting requirements • Refer to E-200 series plans for information regarding mounting heights
NOTES:
CONTRACTOR TO VERIFY FIXTURE FLANGE CONDITIONS WITH SELECTED CEILING SYSTEMS
CONTRACTOR TO COORDINATE ALL CABLES, CONNECTORS AND ACCESSORIES FOR COMPLETE INSTALLATION PER MANUFACTURER'S RECOMMENDATIONS
CONTRACTOR TO PROVIDE CONTINUOUS BLOCKING AS REQUIRED
ALL LED FIXTURES SHALL BE DLC (DESIGN LIGHTING CONSORTIUM) OR ENERGY STAR CERTIFIED